Mt. Morgan JOB SAFETY AND ENVIRONMENTAL ANALYSIS

Laboratory Compressed Air System and Pressure Vessel Statutory Inspection

Job Safety and Environmental Analysis  ·  Heritage Minerals  ·  Mt. Morgan Processing Plant

| Document number | JSEA-PRO-LAB-305-014 |
| --- | --- |
| Work instruction | SWI-PRO-LAB-305-014 Laboratory Compressed Air System and Pressure Vessel Statutory Inspection |
| Parent procedure | HM-PRC-VXX-PRO216 Laboratory Services, Safety and Quality |
| Area | 305 Laboratory Services |
| Classification | Safety-critical |
| Register line | JSEA-PRO-LAB-305-014 in HM-MMM-WHS-REG-JSEA-PRO-updated_10, tab JSEA_LAB |
| Process owner | Heritage Mineral Operations · Business unit Mt. Morgan |
| Document owner | Process Operations Superintendent |
| Document approver | Process Manager |
| Revision | Rev 0 |
| Date | 11 August 2026 |
| Prepared by | GGT (cost code 4034-033) |
| Reviewed by | ________________________ |
| Approved by | ________________________ |

# 1  PURPOSE / SCOPE

This job safety and environmental analysis covers the task laboratory compressed air system and pressure vessel statutory inspection in 305  Laboratory Services at the Mt. Morgan processing plant. It identifies the hazards at each step of the task, the controls required, and the residual risk once those controls are in place.

- Operate the laboratory compressed air system and manage the pressure vessel statutory inspection.

- The 600 L air receiver is a registered pressure vessel in Queensland. Its inspection is a legal obligation before it is put into service, not a maintenance preference.

It is read with work instruction SWI-PRO-LAB-305-014, which gives the step-by-step method, and with HM-PRC-VXX-PRO216 Laboratory Services, Safety and Quality, the procedure this task sits under.

# 2  RESPONSIBILITIES

| Role | Responsibilities |
| --- | --- |
| Operator / Metallurgical Technician | Only carry out this task where competent and authorised to do so. Wear the PPE listed in Section 5 without exception. Stop the task and report immediately if any control in Section 4 is not in place. Record the work accurately. Never invent or back-fill a result that was not obtained. |
| Supervisor / Coordinator | Ensure the safety of all personnel carrying out this task. Understand that much of the plant is automated and equipment may start or stop without warning. Confirm the task is authorised and that the area is fit before it starts. Ensure this JSEA is communicated to everyone doing the task and that the sign-on sheet is completed. |
| Manager / Superintendent | Ensure all personnel have received adequate training and are competent. Ensure this JSEA is reviewed at the interval in Section 10 and after any incident or change. Approve the risk ranking in Section 4. |

# 3  ABBREVIATIONS / DEFINITIONS

| Term | Meaning |
| --- | --- |
| AVR | Acidification, volatilisation and regeneration - the cyanide recovery step in Area 081 |
| CIL | Carbon in leach |
| CN Free | Free cyanide, determined by silver nitrate titration |
| DO | Dissolved oxygen |
| HCN | Hydrogen cyanide gas |
| JSEA | Job safety and environmental analysis - this document |
| P80 | The screen size through which 80 per cent of the material passes |
| PPE | Personal protective equipment |
| ReCYN | The resin-in-pulp cyanide and metal recovery process used in Areas 041, 051, 071 and 081 |
| SWI | Standard work instruction - the step-by-step document that sits under this JSEA |
| SWP | Standard work procedure - the circuit-level procedure this task sits under |
| TSF | Tailings storage facility |
| WAD CN | Weak acid dissociable cyanide |

# 4  POTENTIAL HAZARDS

| Scale | Values |
| --- | --- |
| Probability | 1 Rare 2 Unlikely 3 Possible 4 Likely 5 Almost certain |
| Consequence | 1 Insignificant 2 Minor 3 Moderate 4 Major 5 Catastrophic |
| Risk rank | Probability x Consequence. 1-4 Low 5-9 Medium 10-14 High 15-25 Extreme. Scored after the controls in the same row are in place. |

| Job step | Hazards identified | Controls required | P | C | Risk | Actioned by |
| --- | --- | --- | --- | --- | --- | --- |
| 1. Confirm the receiver is registered and its statutory inspection is current BEFORE it is put into service. An uninspected registered vessel must not be pressurised. | Release from a pressurised sample line, hose or fitting Contact with an agitator, sample cutter, pump or screen that starts without warning | Confirm the sample line is not blocked before opening. Open slowly and stand clear of the discharge path. Report any weeping fitting rather than tightening it under pressure. Much of the plant is automated and equipment can start or stop without warning. Guards confirmed in place before approaching. Control room notified before the round starts and again on completion. Isolation and lock-out before any guard or cutter housing is opened. | 2 | 5 | 10 HIGH | Laboratory Technician |
| 2. Drain the receiver and dryer trap daily, standing clear of the discharge. | Release from a pressurised sample line, hose or fitting | Confirm the sample line is not blocked before opening. Open slowly and stand clear of the discharge path. Report any weeping fitting rather than tightening it under pressure. | 2 | 4 | 8 MEDIUM | Laboratory Technician |
| 3. Record the drain. Undrained condensate corrodes the vessel from the inside where it cannot be seen. | Release from a pressurised sample line, hose or fitting | Confirm the sample line is not blocked before opening. Open slowly and stand clear of the discharge path. Report any weeping fitting rather than tightening it under pressure. | 2 | 4 | 8 MEDIUM | Laboratory Technician |
| 4. Check the oil level and the intake filter at the set interval. | Release from a pressurised sample line, hose or fitting | Confirm the sample line is not blocked before opening. Open slowly and stand clear of the discharge path. Report any weeping fitting rather than tightening it under pressure. | 2 | 4 | 8 MEDIUM | Laboratory Technician |
| 5. Confirm the pressure relief valve has been tested within its interval and is not painted over or obstructed. | Release from a pressurised sample line, hose or fitting Contact with an agitator, sample cutter, pump or screen that starts without warning | Confirm the sample line is not blocked before opening. Open slowly and stand clear of the discharge path. Report any weeping fitting rather than tightening it under pressure. Much of the plant is automated and equipment can start or stop without warning. Guards confirmed in place before approaching. Control room notified before the round starts and again on completion. Isolation and lock-out before any guard or cutter housing is opened. | 2 | 5 | 10 HIGH | Laboratory Technician |
| 6. Never isolate, block or adjust a relief valve. | Release from a pressurised sample line, hose or fitting | Confirm the sample line is not blocked before opening. Open slowly and stand clear of the discharge path. Report any weeping fitting rather than tightening it under pressure. | 2 | 4 | 8 MEDIUM | Laboratory Technician |
| 7. Depressurise and isolate before any work on the receiver or its fittings. | Release from a pressurised sample line, hose or fitting Contact with an agitator, sample cutter, pump or screen that starts without warning | Confirm the sample line is not blocked before opening. Open slowly and stand clear of the discharge path. Report any weeping fitting rather than tightening it under pressure. Much of the plant is automated and equipment can start or stop without warning. Guards confirmed in place before approaching. Control room notified before the round starts and again on completion. Isolation and lock-out before any guard or cutter housing is opened. | 2 | 5 | 10 HIGH | Laboratory Technician |
| 8. Keep the inspection certificate with the asset register and diarise the next inspection. | Release from a pressurised sample line, hose or fitting | Confirm the sample line is not blocked before opening. Open slowly and stand clear of the discharge path. Report any weeping fitting rather than tightening it under pressure. | 2 | 4 | 8 MEDIUM | Laboratory Technician |

# 5  PPE

Standard PPE is worn for all normal operations in the Mt. Morgan gold processing plant. The following is required for this task.

- Hard hat

- Safety glasses

- High-visibility long-sleeved shirt and long trousers

- Safety boots

- Gloves appropriate to the task

- Personal HCN gas monitor, calibrated and in test date

- Chemical splash goggles and face shield

- Nitrile rubber gloves

- Nitrile PVC boots

- Chemical resistant suit

- Full or half gas mask with A2B2E2K2P3 cartridge, carried and available for immediate use

- Acid-resistant gloves, apron and face shield

- Chemical splash goggles

# 6  PROCEDURE

6.1  Introduction

Warning: many operations on the gold processing plant are automated and equipment may start or stop without warning. It is the operator's responsibility to ensure the safety of all personnel working on the plant at all times.

Frequency: Daily drain; statutory inspection at the regulated interval.

6.2  Job steps

1.  Confirm the receiver is registered and its statutory inspection is current BEFORE it is put into service. An uninspected registered vessel must not be pressurised.

2.  Drain the receiver and dryer trap daily, standing clear of the discharge.

3.  Record the drain. Undrained condensate corrodes the vessel from the inside where it cannot be seen.

4.  Check the oil level and the intake filter at the set interval.

5.  Confirm the pressure relief valve has been tested within its interval and is not painted over or obstructed.

6.  Never isolate, block or adjust a relief valve.

7.  Depressurise and isolate before any work on the receiver or its fittings.

8.  Keep the inspection certificate with the asset register and diarise the next inspection.

Equipment required:

- Pneumark PM 7.5 kW compressor, 43 cfm

- 600 L air receiver

- Refrigerated dryer

- Pressure relief valve

- Statutory inspection records

- Service log

# 7  FLOWCHART

Not reproduced in this document. The step sequence is in work instruction SWI-PRO-LAB-305-014 Section 6, which is the controlled version of the method.

# 8  TRAINING

Every person carrying out this task has been through this JSEA at a communication session recorded on the sign-on sheet at the end of this document, and is trained and signed off against work instruction SWI-PRO-LAB-305-014.

- Site induction, current.

- Cyanide awareness and gas detection competency where the area requires it.

- Working at height competency where the task requires it.

- Competency in the determinations and calculations carried out in this task.

# 9  REFERENCE

- ILS quote Q0023979: Pneumark PM 7.5 kW, 43 cfm, 600 L receiver. A registered pressure vessel in Queensland - statutory inspection applies

- Heritage register line JSEA-PRO-LAB-305-014, tab JSEA_LAB / SWI-LAB

# 10  REVIEW

This JSEA is reviewed every 12 months, and immediately after any incident, near miss, plant change or change to the schedule affecting this task.

# JSEA COMMUNICATION AND AWARENESS

| Presented by | ________________________ |
| --- | --- |
| Date | ________________________ |
| JSEA reference | JSEA-PRO-LAB-305-014 |

| Name | Position | Department | Signature |
| --- | --- | --- | --- |